Copyright 2016 by The American Institute of Architects (AIA)

Exclusively published and distributed by Deltek, Inc. for the AIA

This Product MasterSpec Section is licensed by Deltek, Inc. to Lencore ("Licensee").

This Product MasterSpec Section modifies the original MasterSpec text and does not include the full content of the original MasterSpec Section.

Revisions made to the original MasterSpec text are made solely by the Licensee and are not endorsed by, or representative of the opinions of, Deltek or The American Institute of Architects (AIA). Neither AIA nor Deltek are liable in any way for such revisions or for the use of this Product MasterSpec Section by any end user. A qualified design professional should review and edit the document to suit project requirements.

For more information, contact Lencore, 839 New York Ave., Suite 21, Huntington, NY 11743; Phone: (516) 682-9292; Website: www.lencore.com; Email: info@lencore.com.

For information about MasterSpec, contact Deltek at (800) 424-5080 or visit masterspec.com.

SECTION 275119.11 - SOUND MASKING SYSTEMS

TIPS:

To view non-printing Editor's Notes that provide guidance for editing, click on Masterworks/Single-File Formatting/Toggle/Editor's Notes.

To read detailed research, technical information about products and materials, and coordination checklists, click on Masterworks/Supporting Information.

Access Product MasterSpec Sections:

<Double click here to view the list of manufacturer Sections available at ProductMasterSpec.com.>

Revise this Section by deleting and inserting text to meet Project-specific requirements.

GENERAL

SUMMARY

Section Includes:

Networked sound-masking system.

Non-networked sound-masking system.

Wire and cable.

Related Requirements:

Retain subparagraphs below to cross-reference requirements Contractor might expect to find in this Section but are specified in other Sections.

Section 095123 "Acoustical Tile Ceilings."

Section 270528 "Pathways for Communications Systems" for conduits, wireways, surface pathways, innerduct, boxes, enclosures, and cabinets serving communications systems.

Section 284621.11 "Addressable Fire-Alarm Systems" for mute sound masking in the event of a fire emergency.

Section 284621.13 "Conventional Fire-Alarm Systems" for mute sound masking in the event of a fire emergency.

REFERENCES

ANSI S1.4, "Specification for Sound Level Meters."

ANSI S1.6, "Preferred Frequencies and Filter Band Center Frequencies for Acoustical Measurements."

ANSI S1.11, "Octave-Band and Fractional-Octave-Band Analog and Digital Filters."

Retain "ANSI 709.1" Paragraph below for networked connected sound-masking systems.

ANSI 709.1, "Control Network Protocol Specification" for standards related to open platforms.

ASTM E1374-06, "Standard Guide for Open Office Acoustics and Applicable ASTM Standards."

ASTM E1573-18, "Standard Test Method for Measurement and Reporting of Masking Sound Levels Using A-Weighted and One-Third-Octave-Band Sound Pressure Levels."

NFPA 72, "National Fire Alarm and Signaling Code."

UL 1310, "Standard for Class 2 Power Units."

UL 1480, "Standard for Speakers for Fire Alarm and Signaling Systems, Including Accessories."

UL 2043, "Standard for Fire Test for Heat and Visible Smoke Release for Discrete Products and Their Accessories Installed in Air-Handling Spaces."

UL 2572, "Standard for Mass Notification Systems."

UL 60065, "Standard for Audio, Video and Similar Electronic Apparatus - Safety Requirements."

UL 6500, "Standard for Audio/Video and Musical Instrument Apparatus for Household, Commercial, and Similar General Use."

ACTION SUBMITTALS

Product Data: For each type of product.

Include construction details, material descriptions, dimensions, profiles and finishes of individual components.

Include rated capacities, operating characteristics, electrical characteristics, and furnished specialties and accessories.

Nationally recognized testing laboratory listing data for plenum-mounted and rack-mounted equipment.

Shop Drawings: For sound-masking systems.

Include plans, elevations, sections, and mounting details for all system components. Provide schematics of system design including floor plan indicating quantity, type, and location of components.

Include details of equipment assemblies and installation instructions. Indicate dimensions, weights, loads, required clearances, method of field assembly, components, and location and size of each field connection.

Include diagrams for power, signal, and control wiring.

CLOSEOUT SUBMITTALS

Operation and Maintenance Data:

Provide as-built drawings of the system including schematics and floor plans indicating quantity, type, and location of components, cabling, and accessories.

Operation and maintenance manuals.

Provide warranty documentation, with start date(s) and service contract(s).

Retain "Software and Firmware Operational Documentation" Paragraph below for PC-based control systems.

Software and Firmware Operational Documentation:

Inventory of system components, with model and serial numbers for each.

Software operating and upgrade manuals.

Program Software and System Settings Backup: On digital media complete with data files. Provide electronic backup file of all system settings.

Device address list.

Printout of software application and graphic screens.

Provide login ID and password(s) to access control functions on the graphical user interface, if applicable.

QUALITY ASSURANCE

Installer Qualifications: Factory qualified and certified to install products listed.

Responsible for system specified and single contact point for Architect, Consultant, Fire Protection Engineer, and/or Owner with respect to sound-masking work specified.

Experienced in design, fabrication, installation, checkout, and warranty contract management of sound-masking systems.

Obtain required permits.

Follow applicable codes, including regulatory testing and certifications.

Equipment and associated hardware fabricated and installed in accordance with manufacturer's instructions.

Configuration and commissioning by an authorized manufacturer representative or their approved agent.

COORDINATION

Coordinate quantity and arrangement of sound-masking system components with ceiling space configuration and with components occupying ceiling space, including structural members, pipes, air-distribution components, raceways, cable trays, luminaires, and other items.

Retain paragraph below if raceway system and sound-masking system will be installed by two different contractors.

Coordinate raceway system material, routing and locations with [Division 26 Contractor] [General Contractor] [Construction Manager].

DELIVERY, STORAGE AND HANDLING

Deliver in manufacturer's original unopened and undamaged packages with manufacturer's labels legible and intact.

Store and handle in strict compliance with manufacturer's written instructions and recommendations. Protect from moisture during shipping, storage, and handling.

Inspect manufacturer's packages upon receipt.

WARRANTY

When warranties are required, verify with Owner's counsel that warranties stated in this article are not less than remedies available to Owner under prevailing local laws.

Manufacturer's Special Warranty: Manufacturer agrees to repair or replace sound-masking loudspeaker control units and loudspeakers that fail in materials, workmanship, or performance within one year (warranty period) from date of installation.

At Closeout, provide to Owner an executed copy of manufacturer's standard limited warranty against manufacturing defects, outlining terms, conditions, and exclusions from coverage.

System components for sound masking must carry a minimum 10-year warranty. Warranty statements must be submitted prior to notice to proceed.

Verify available warranties and warranty periods.

Warranty Period: [Ten] <Insert number> years from date of Substantial Completion.

PRODUCTS

Manufacturers and products listed in this Section are neither recommended nor endorsed by the AIA or Deltek. Before selecting manufacturers and products, verify availability, suitability for intended applications, and compliance with minimum performance requirements. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

Product options commonly available from manufacturers are included in square brackets throughout the Section Text. Not every manufacturer listed can provide every option offered; verify availability with manufacturers. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."

PERFORMANCE REQUIREMENTS

Source Limitations: Obtain components for sound-masking system from a single source.

Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

Compliance Standard: Fabricate and label electronic components to comply with UL 60065 or UL 1419.

Retain "Compliance Standard" Paragraph below if interface with fire alarm system is required by Project.

Compliance Standard: Fabricate and label components to comply with UL 2572, in order to interface with a Fire Alarm Control Unit (FACU).

Wire, cable, devices, and assemblies installed in air-handling spaces to be plenum rated, complying with NFPA 70 requirements for rate of heat-release and smoke-release characteristics. Tests for these requirements to be in accordance with UL 2043.

NETWORKED SOUND-MASKING SYSTEMS

Description: Networked decentralized architecture [sound-masking] [sound-masking and paging] [sound-masking, paging, and background music] system with digital control of addressable system devices. Digital network controls at control panel include adjustments and monitoring and display of current settings for sound-masking and paging of loudspeaker controls, associated network devices, and control panel components.

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

Link to i.Net Product Page: https://www.lencore.com/products/soundmasking-products/i-net/.

Link to Gold Product Page: https://www.lencore.com/products/soundmasking-products/gold/.

Basis-of-Design Product: Subject to compliance with requirements, provide Lencore; [i.Net][Gold][Silver].

Standard: Comply with ASTM E1374.

Network:

Provide an Ethernet LAN to connect controller/gateways to a PC running a Microsoft Windows operating system, macOS, or iOS.

Ethernet 10BASE-T is generally the minimum that meets data transmission requirements to control a sound-masking system. Higher-speed networks may be needed by the sound-masking system options and project requirements.

Ethernet Protocols: Comply with and be compatible with [10BASE-T] <Insert Ethernet standard> routers and networks.

Network communications protocol to be [IP] <Insert communications protocol>.

Network controls to be available at the control panel [or] [and] using a PC connected to the control network,

Network Control Panel. Single, system control for entire building or buildings by providing operation of multiple system components from a single, central location. Control Panel should be 1RU or 2RU maximum.

Connections.

Comply with UL 60065.

Power Supply: NFPA 70, Class 2.

Ethernet Connection: TIA 485.

Serial Connection: RS-232 port.

Output to Loudspeaker Control Units: NFPA 70, Class 2.

The minimum frequency range to mask intruding speech is approximately 250 Hz to 4 kHz, and the loudspeakers should provide adequate output for at least one octave below this range to enhance natural reproduction of the electronically generated sound.

Sound-Masking Performance: Digital signal processing (DSP) technology for masking sound generation and output adjustment of masking signals.

Masking Sound: Generated via a truly random, non-deterministic digital process with no repeat cycle within a 24-hour period.

System Requirements:

Single Control Unit: Capable of addressing entire system. Multiple control units not acceptable.

Integrated Sound-Masking Digital Signal Processors (DSPs): Utilize an open platform network technology, meeting open control standards with web appliances, browser interfaces, infrared remote controls, and internet access capable.

Capable of separately and independently configuring zones for sound masking via the network, zoned through its singular central control.

Retain "Sound-Masking System Shutdown" if an interface to fire alarm system is required by Project. Specific to the Networked Lencore i.Net System only.

Sound-Masking System Shutdown: Through interface with FACU as described in Section 283100 "Intrusion Detection."

Compliance: UL 2572.

Control System: Capable of using TCP/IP for intelligent building integration.

Standards for Open Platform: Comply with ANSI/CEA 709.1.

US Army Corp.'s Unified Facilities Guide Specifications:

UFGS 25 10 10, "Utilities Monitoring and Control System."

UFGS 23 09 23, "Direct Digital Control for HVAC and Other Local Building Controls."

Multi-drop network system; point-to-point systems are unacceptable.

System Tuning: Through [network] [hand-held remote] [keypad].

Complete diagnostics capability of entire system functions including diagnostics of network, hubs, nodes, routers, DSP, relays, memory, circuitry, amplifiers, and power.

Report entire settings for each zone, indicating at a minimum the volume, contour, equalization, diagnostics, and zones and channel groupings.

Diagnostics and remote administration via a standard web browser.

Capable of naming network nodes, channels, zones, and external audio sources via its integrated graphical user interface.

Equalizer: 30-Band[ third-octave compilable via DSP].

Sound-masking adjustment for each loudspeaker control unit:

Masking Sound: 20 Hz to 20 kHz, with equalizers for adjusting the masking-sound spectrum at third-octave resolution.

Masking-Sound Volume Adjustment: Digital control,[ adjustable in 0.5-dBA increments over the range of 34 to 82.5 dBA] <Insert values> or a continuous adjustment within that range.

Twenty-eight (28) preset contour options. Adjust contour from minus 14 to plus 14.

Paging Inputs: Provision for the devices listed below, with analog-to-digital conversion of audio signals.

Telephone.

Input Impedance: 600 ohm.

Operating Loop Current: 13 to 120 mA.

Dynamic Range: 82 dB.

Receive THD: Minus 82 dB.

Auxiliary.

Input Impedance: 10 kiloohms.

Input Level: 3.5 V(rms) maximum.

Gain, Max: 6 dB.

Microphone.

Input Impedance: 600 ohm.

Input Level: 70 mV maximum.

Gain, Max: 60 dB.

Paging Performance:

Paging Volume Control: 34 to 83 dB in 1 dB steps with mute setting.

One-octave signal equalizer, with 10 bands, 31.25 Hz to 16 kHz.

[Four] <Insert number> channels per Operating Platform (OP).

Capable of digitally assigning any group of masking zones to a selected channel.

Volume Control: Selectable in 1 dB steps.

Enclosure: 1 RU rack enclosure for mounting in a rack unit or on a wall.

Control Network Software: Microsoft, Windows, macOS, or iOS based.

Description of Functions:

Communicate with network control panel(s) to assign device addresses and to configure network hardware.

For "Security" Subparagraph below, see "Security" Article in the Evaluations for AES encryption information.

Security: 128-bit AES encryption and user passwords.

Setup data to be saved in electronic and printed formats.

Typically, the loudspeaker control unit is in the same enclosure as the loudspeaker; some manufacturers use separate enclosures. Indicate preferences on Drawings.

Sound-Masking Loudspeaker Control Unit: Addressable, connected to the sound-masking system control network. Unit has no physical controls; all settings to be from the network control panel.

Masking-Sound Generator: Digital, solid-state, random sequence noise generator, stable in sound spectrum and output level, and containing the following:

Electronic sound amplifier and equalizers for shaping the masking-sound spectrum, complying with ASTM E1374.

The minimum frequency range to mask intruding speech is approximately 250 Hz to 4 kHz, and the loudspeakers should provide adequate output for at least one octave below this range to enhance natural reproduction of the electronically generated sound.

Masking Sound: [20 Hz to 20 kHz] <Insert frequencies>, with equalizers for adjusting the masking-sound spectrum at third-octave resolution.

Masking-Sound Volume Adjustment: At least 10 steps at 0.5 dB each, or a continuous adjustment within that range.

Independent zoning of sound masking[ and paging] [, paging, and background audio].

Retain "Inline Speakers" Subparagraph below if individual speaker adjustment is required by Project.

Inline Speakers: Speakers with independent potentiometer allowing individual speaker adjustment control outside of networked zoned controls.

Paging Performance:

Music-Page Interface (MPI): Device with direct microphone, second line-level microphone, or analog phone input.

Diagnostic functions specified at the network control panel.

Enclosure: One RU high, rack mounted, metal enclosure.

Sound-Masking Loudspeakers: Connected to a loudspeaker control unit.

Cone Type: 4 inches (102 mm) in diameter with 1-inch (25-mm) voice coil and minimum 10-oz. (283-g) ceramic magnet, mounted in an acoustic enclosure ensuring delivery of a broad frequency spectrum.

Rated Output Level: 10 W.

Dispersion Angle: 120 degrees.

Sensitivity: 88-dB sound-pressure level (SPL) at 1 W/m on the reference axis.

Audio Output: 83 dB, maximum for both masking sound and paging/music.

Frequency Response: Plus or minus 3 dB from 85 to 13,000 Hz.

Enclosure: Metal acoustic enclosure, housing the loudspeaker, its connections, and controls.

Mounting:

For plenum mounting, arrange units for upward dispersion, suspended from the building structure above the ceiling; adjustable, not less than 20 inches (510 mm) from finished ceiling.

For flush-with-ceiling mounting, arrange units for downward dispersion and equip with a perforated grill and accessories required for mounting in the suspended ceiling system.

See Lencore's extensive speaker options here: https://www.lencore.com/inet-data-sheets/.

Power Supplies: Comply with UL 1310, Class 2.

NON-NETWORKED SOUND-MASKING SYSTEM

Description: Single, non-networked, self-contained, plenum-mounted loudspeaker with [sound-masking] [sound-masking and paging] [sound-masking, paging, and background music] generator and associated controls. System includes electronic noise generators, amplifiers, wiring, loudspeakers, controls, and components to generate, amplify, distribute, and reproduce digitally synthesized and stabilized background sound masking to improve speech privacy in zones of coverage.

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

Additional information regarding Lencore Classic can be found here: https://www.lencore.com/products/soundmasking-products/classic/.

Basis-of-Design Product: Subject to compliance with requirements, provide Lencore; Classic.

Standard: Comply with ASTM E1374.

Standalone Sound-Masking Loudspeakers:

Power Supply: NFPA 70, Class 2.

House loudspeaker and controls to be in a metal acoustic enclosure.

For plenum mounting, arrange units for upward dispersion, suspended from the building structure above the ceiling; adjustable, not less than 20 inches (510 mm) from finished ceiling.

For flush-with-ceiling mounting, arrange units for downward dispersion and equip with a perforated grill and accessories required for mounting in the suspended ceiling system.

Masking Sound: Digital, random sequence, noise generator, electronic sound amplifier and filters for adjusting the sound spectrum.

Masking Sound: 125 Hz to 8 kHz.

Masking-Sound Volume Adjustment: At least 10 steps, plus a continuous adjustment.

Loudspeaker:

Cone Type: 4 inches (102 mm) in diameter with 1-inch (25-mm) voice coil and minimum 10-oz. (280-g) ceramic magnet, mounted in an acoustic enclosure.

Impedance: 16 ohms.

Rated Output Level: 10 W rms.

Dispersion Angle: 120 degrees.

Sensitivity: 88-dB sound-pressure level (SPL) at 1 W/m on the reference axis.

Audio Output: 87 dBA, maximum for both masking sound and paging/music audio signals.

Frequency Response: 85 to 13,000 Hz.

Retain "Remote Central Volume Control (RCVC)" Subparagraph below if required by Project.

Remote Central Volume Control (RCVC):

Operates as central volume control from which universal volume adjustments can be made remotely for a minimum 50 main units and covering up to 33,000 sq. ft. (3065 sq. m).

Equipped with a 10-step volume control, an additional continuous volume control, and central volume remote adjustment control (as described above).

Consists of individual self-contained noise generator, audio amplifier, and loudspeaker in damped aluminum enclosure.

All solid-state components with CMOS/MSI digital random sequence noise generator, electronic amplifier, and filter for active spectrum shaping.

Power Input: 16 to 18 V(ac).

Capable of driving one secondary loudspeaker.

Sound Output Range: 41 to 86 dBA.

Independent and separate volume control for paging/music.

WIRE AND CABLE

Retain one of first two paragraphs below. Retain first paragraph to specify all cable in Section 271513 "Communications Copper Horizontal Cabling" and for options not described below.

Comply with Section 271513 "Communications Copper Horizontal Cabling" for balanced twisted pair cabling.

Category 5e Twisted Pair Cable: Four-pair, balanced-twisted pair cable, certified to comply with transmission characteristics of Category 5e cable at frequencies of up to 100 MHz.

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

Manufacturers: Subject to compliance with requirements, provide products by one of the following:

AMP NETCONNECT; a TE Connectivity Ltd. company.

Belden Inc.

Berk-Tek Leviton; a Nexans/Leviton alliance.

CommScope, Inc.

General Cable; Prysmian Group North America.

Hitachi Cable America Inc.

Mohawk; a division of Belden Networking, Inc.

SYSTIMAX Solutions; a CommScope Inc. brand.

West Penn Wire.

<Insert manufacturer's name>.

100-ohm, 24 AWG solid copper.

[Unshielded twisted pairs (UTP)] [Shielded twisted pairs (FTP)] [Screened twisted pairs (F/UTP)] [Screened and shielded twisted pairs (F/FTP)].

[Riser] [Plenum] rated.

Loudspeaker Wire and Cables:

"Plenum-Rated, Paired Cable" Subparagraph below describes common conductor used for loudspeakers. Other conductor sizes, configurations, and insulation types are available.

Plenum-Rated Paired Cable: NFPA 70, Type CMP.

One pair, twisted, [No. 16 AWG, stranded (19x29)] [No. 18 AWG, stranded (19x30)] <Insert requirement> tinned-copper conductors.

PVC insulation.

Unshielded.

PVC jacket.

NFPA 262 includes the standard flame-resistance test criteria in common use for cables and conductors.

Flame Resistance: Comply with NFPA 262.

"Lead Content" Subparagraph below applies to LEED v4 for Healthcare, MRc "PBT Source Reduction-Lead, Cadmium, and Copper."

Lead Content: Less than 300 parts per million.

Control-Circuit Conductors:

Class 2 Control Circuits: Stranded copper, Type THHN/THWN-2, complying with UL 83 in raceway.

EXECUTION

INSTALLATION

Comply with NECA 1.

Install in accordance with manufacturer's instructions based upon approved system design and submittals. Follow manufacturer's installation manual.

General Contractor: Responsible for supplying any conduit, which may be required to complete system installation in accordance with specifications and local building codes.

Loudspeaker Assemblies: Suspend with chains from building structure above ceilings, so bottom of assembly is 6 to 8 inches (150 to 200 mm) above upper plane of finished ceiling material. Use eyebolts on speaker assemblies for attachment. Suspend independently from structure, not to supports for components of other building systems.

Retain "Loudspeaker Connections" Paragraph for zoned systems.

Loudspeaker Connections: For two- or three-channel systems, connect loudspeaker assemblies alternatively, so masking sound is redundant throughout coverage zones.

Retain one of two "Wiring Method" paragraphs below and coordinate with Drawings. Delete both paragraphs if wiring methods for system are indicated on Drawings.

Wiring Method: Install cables in raceways and cable trays, except within consoles, cabinets, desks, and counters and unless otherwise indicated.

Retain one or both of first two subparagraphs below to make exceptions to the wiring method specified above.

Except raceways are not required in accessible indoor ceiling spaces and attics.

Except raceways are not required in hollow gypsum board partitions.

Conceal raceways and wiring, except in unfinished spaces.

Wiring Method: Conceal conductors and cables in accessible ceilings, walls, and floors where possible.

Retain first subparagraph below if retaining option for unenclosed wiring method.

Install plenum cable in environmental air spaces, including plenum ceilings.

Comply with requirements for raceways and boxes specified in Section 260533 "Raceway and Boxes for Electrical Systems."

Comply with requirements in Section 271513 "Communications Copper Horizontal Cabling."

Wiring within Enclosures: Bundle, lace, and train conductors to terminal points with no excess and without exceeding manufacturer's limitations on bending radii. Provide and use lacing bars and distribution spools.

Retain "Exposed Cable" Paragraph below for cable wiring method.

Exposed Cable: Install parallel to building lines, follow surface contours, and support as recommended by manufacturer.

Coordinate "Grounding" Paragraph below with Drawings.

Grounding: As recommended by manufacturers unless more stringent requirements are indicated. Ground equipment and conductors to eliminate shock hazard and to minimize ground loops, common-mode returns, noise pickup, cross talk, and other impairments with a maximum of 5 ohms to ground at main equipment location.[ Measure, record, and report ground resistance.]

Impedance Matching: For system components, including connecting cable, provide end-to-end level and impedance-matched signal paths. Use matching networks and balancing devices at connections where necessary to avoid mismatches.

Splices, Taps, and Terminations: Make splices, taps, and terminations on numbered terminal strips in junction, pull, and outlet boxes; terminal cabinets; and equipment enclosures.

Retain paragraph below if interface with fire alarm system is required by Project.

Final connection to FACU will be completed by fire alarm system installer.

IDENTIFICATION

Comply with requirements for identification specified in Section 260553 "Identification for Electrical Systems."

Use color-coded conductors, and apply wire- and cable-marking tape to designate wires and cables, so media are identified in coordination with system wiring diagrams.

Retain paragraph below for addressable and zoned systems.

Label loudspeakers as to channel, zone, and address.

FIELD QUALITY CONTROL

Retain one of first four paragraphs below. Retain first "Testing Agency" Paragraph below if Owner will hire an independent testing agency.

Testing Agency: Owner will engage a qualified testing agency to perform tests and inspections.

Retain "Testing Agency" Paragraph below to require Contractor to hire an independent testing agency.

Testing Agency: Engage a qualified testing agency to perform tests and inspections.

Retain "Manufacturer's Field Service" Paragraph below to require a factory-authorized service representative to perform tests and inspections.

Manufacturer's Field Service: Engage a factory-authorized service representative to test and inspect components, assemblies, and equipment installations, including connections.

Retain "Perform tests and inspections" Paragraph below to require the Contractor to perform tests and inspections. Retain option to require Contractor to arrange for the assistance of a factory-authorized service agent.

Perform tests and inspections[ with the assistance of a factory-authorized service representative].

Retain "Tests and Inspections" Paragraph below to describe tests and inspections to be performed.

Tests and Inspections:

Operational Test: Start system to confirm proper operation. Remove malfunctioning units, replace with new units, and retest. Make initial sound-spectrum and -level adjustments for each zone.

Inspection: Verify that units and controls are properly labeled and interconnecting wires and terminals are identified.

Pretesting: Tune, align, and adjust system, and pretest components, wiring, and functions to verify compliance with specified material, installation, and performance requirements. Correct deficiencies and retest until satisfactory performance and conditions are achieved.

Retain masking-sound power level minimum range based on estimated ambient sound level.

Masking Sound-Power Level Adjustments: Adjust independently for each space to minimum level between [40] [47] and 50 dBA that will provide speech privacy between adjacent workstations while complying with other system requirements.

Final Acceptance Testing: Provide a minimum of 10 days' notice of acceptance test performance schedule. Schedule tests after pretesting has been successfully completed.

ASTM E1130 is the most commonly used testing protocol. See "Applicable Standards" Article in the Evaluations for additional guidance.

Perform sound-masking evaluation tests in accordance with [ASTM E1130] [ASTM E1573], with measurements and calculations in accordance with ANSI S3.5. Report test results in accordance with the requirements in [ASTM E1130] [ASTM E1573].

Tests and Calibration Conditions: Spaces to be completely furnished but unoccupied; lights and HVAC systems to be on; HVAC system testing and balancing to be completed; and electronic ballasts, lighting relay panels, and low-voltage transformers to be in place.

Test Conditions: Complying with ASTM E1130 and calculated in accordance with ANSI S3.5.

Instrumentation: Use a professional-quality, sound-level meter with octave-band filters and documentation of recent calibration against recognized standards. Comply with ANSI S1.4-1.

Record test observations, readings, and corrective actions.

System Tests: Include the following for each system zone:

Loudspeaker Circuit Impedance Test: Measure impedance at 1000 Hz with amplifier disconnected, using a professional impedance meter or bridge. Locate and correct faults denoted by abnormal readings.

Ambient Sound-Level Tests: With system off, measure ambient sound level in one-third octave bands. Also measure ambient sound level as a single, wide-band, A-weighted reading.

System Noise Test: With masking-noise signal on and amplifiers adjusted at a working level 10 dB above ambient sound level, check for hum, buzz, rattle, or other operating deficiencies.

Spatial Uniformity Test: Measure sound level at locations no greater than 15 ft. (4.6 m) o.c. throughout covered spaces to determine compliance with specified performance level.

Frequency Response Adjustment and Test: Adjust one-third octave frequency bands and other unit filters to provide response. Adjust to meet requirement of space speech intelligibility and quality of background sound. Comply with ANSI S3.2, CTA 426, and ASTM E1110.

Retain one of first two subparagraphs below, or replace with text recommended by the sound-masking system designer. The subparagraphs represent a prescriptive method of achieving sound-masking results that should comply with the specified standard. Commissioning of the sound-masking system may require additional adjustments. See the Evaluations for samples of system-masking curve setting tables.

Adjust level of masking sound that is appropriate for the area and the overall volume.

Adjust level of masking sound for each space, so one-third octave band centered at 500 Hz has final selected sound-power level for that space. Measure deviation from listed values in one-third octave bands from 100 to 1000 Hz. Measured values must not deviate from those listed by more than four dB for open-plan areas and eight dB for enclosed offices. The total of individual band deviations in eight bands must not exceed 16 dB for open-plan areas and 30 dB for enclosed offices.

Walk-Through Test: People in covered spaces cannot discern loudspeaker locations.

Where required, space to comply with HIPPA (45 CFR, Parts 160 and 164) for privacy.

Where required, space to comply with the Gramm-Leach Bliley Act to protect consumer personal and financial information in open office layouts.

Retest: Correct deficiencies identified by tests and observations, and retest until compliance with specified requirements is achieved.

Recording Control Settings and System Adjustments: Record final control settings and programming, and final tap setting of loudspeaker-matching transformers. Record final sound-level measurements and observations.

ADJUSTING

Occupancy Adjustments: When requested within [12] <Insert number> months of date of Substantial Completion, provide on-site assistance in adjusting system to suit actual occupied conditions. Provide up to [two] <Insert number> visits to Project during other-than-normal occupancy hours for this purpose.

SOFTWARE SERVICE AGREEMENT

Services in this article may not be allowed for publicly funded projects.

Technical Support: Beginning at Substantial Completion, service agreement to include software support for [two] <Insert number> years.

Upgrade Service: At Substantial Completion, update software to latest version. Install and program software upgrades that become available within [two] <Insert number> years from date of Substantial Completion. Upgrading software to include operating system and new or revised licenses for using software.

Upgrade Notice: At least [30] <Insert number> days to allow Owner to schedule and access the system and to upgrade computer equipment if necessary.

DEMONSTRATION

[Engage a factory-authorized service representative to train] [Train] Owner's maintenance personnel to adjust, operate, and maintain services.

END OF SECTION 275119.11